NEXARA

Integrated Management System

Safe Working Procedure — Hot Work

ISO 45001:2018 Clause 8.1.2

| Document Number: | SWP-003 |
| --- | --- |
| Version: | 1.0 |
| Date: | [DD/MM/YYYY] |
| Owner: | [H&S Manager] |
| Approved By: | [Operations Director] |
| Classification: | Confidential |

Revision History

| Version | Date | Description | Author | Approved By |
| --- | --- | --- | --- | --- |
| 1.0 | [DD/MM/YYYY] | Initial Issue | [Author Name] | [Approver Name] |

# 1. Purpose

To control the fire and explosion risks associated with hot work activities including welding, cutting, brazing, soldering, grinding, and any operation producing sparks, flames, or heat.

# 2. Scope

Applies to all hot work operations conducted on [COMPANY NAME] premises or by [COMPANY NAME] employees at external sites. Includes oxy-fuel cutting/welding, electric arc welding (MIG, TIG, MMA), plasma cutting, brazing/soldering, grinding/cutting with abrasive wheels, and use of heat guns or open flames.

# 3. Hazards

- Fire from sparks/molten metal contacting combustible materials

- Explosion in areas with flammable gases/vapours/dusts

- Burns to operator and nearby persons

- Toxic fumes (zinc, cadmium, manganese, chromium from coated/stainless steels)

- UV/IR radiation — arc eye, skin burns

- Electrocution from welding equipment

- Noise — grinding and plasma cutting exceed 85 dB(A)

# 4. Pre-Work Controls

- Obtain a Hot Work Permit (FRM-006 with hot work addendum) — valid for single shift only

- Clear all combustible materials within 11 metres (35 feet) of the work area

- Where combustibles cannot be removed, protect with fire-resistant blankets/screens

- Check for flammable atmospheres — gas test if near tanks, pipes, or drains

- Ensure fire extinguisher (minimum 9L water + CO₂) is within 3 metres of work

- Designate a Fire Watch — trained person with extinguisher for duration of work + 60 minutes after

- Notify the fire alarm monitoring point to prevent false alarm callouts

- Cover/seal floor drains, gaps, and openings where sparks could travel

# 5. During Work

- Operator to wear appropriate PPE: auto-darkening welding helmet (shade 10-13), fire-resistant coveralls, welding gauntlets, safety boots, ear protection where required

- Use welding screens/curtains to protect bystanders from UV radiation

- Ensure adequate ventilation — LEV for indoor welding, RPE if LEV insufficient

- Regularly inspect hoses, regulators, cables, and connections

- Flashback arrestors fitted to all oxy-fuel equipment

- Cylinders stored upright, secured, away from heat sources, with caps when not in use

# 6. Post-Work Fire Watch

The Fire Watch must remain for a minimum of 60 minutes after all hot work ceases. During this period:

a) Continuously patrol the work area and adjacent areas (including floors above/below)
b) Check for smouldering materials, hot spots, and smoke
c) Maintain access to fire extinguisher and communication device
d) If any sign of fire is detected — raise the alarm, evacuate, and call the fire brigade

# 7. Training Requirements

- Hot Work Safety Awareness

- Specific welding process certification (e.g., BS EN ISO 9606)

- Fire extinguisher use

- Fire Watch duties

# 8. Related Documents

- FRM-006: Permit to Work Form

- PRO-011: Emergency Preparedness

- Fire Risk Assessment

- COSHH Assessments for welding fumes